## OP Services -Final
Standardised Architectural Modules
Version : Prefinal | [13 empty] | Doc No. 1240-A-Doc-033
Revised on April 22, 2021
Checklist: Outpatient services - Clinical areas for major eye care specialities
This checklist lists commonly available in most eye hospitals and hence not a complete list. Please add additional area as appropriate
S No | Room Name | Dimension (L X B) in Feet |  |  | Area in Sq.Ft | Description | General OPD | Paediatric Speciality | Cataract Speciality | Glaucoma Speciality | Uvea Speciality | Cornea Speciality | Retina Speciality | Orbit Oculopalsty & Oncology Speciality | Vision rehabilitation Speciality | Neuro Speciality | Contact Lens Speciality | Pre operative workup room | Remarks
I | Patient regiration & coordination area
1 | Patient registration at outpatient clinic |  |  |  | 19.4 | Receiving and coordinating patient consultation and treatment process | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
2 | Waiting area-I |  |  |  | 7 | Waiting area for preliminary exam (Sq.ft per person x no of persons) | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
3 | Waiting area-II |  |  |  | 7 | After dilation & final | ü | ü | ü | ü | ü | ü | ü | ü
4 | Waiting area-III |  |  |  | 7 | Counselling (Sq.ft per person x no of persons) | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
II | Examination area
5 | Standard exam room | 8 | x | 11 | 88 | Used for preliminary and final examination of the patient's eye. | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  | This room size is applicable to exam rooms for adults and chlidren
III | Assessment area
6 | Vision room | 6 | x | 11 | 66 | Check the eye's ability to detect fine details and the quantitative measure of the eye's ability to see an in-focus image at a certain distance. | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  | Vision room is not required in speciality clinics
7 | Refraction room | 6 | x | 11 | 66 | To measure the refractive error, or vision problem | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  | One of the refraction rooms can include Hess chart used for assessing children's vision
8 | Squint examination room | 8 | x | 11 | 88 | Paediatric eye examination |  | ü
9 | Low vision assesement room | 5 | x | 11 | 55 | Examination and evaluation procedure | [8 empty] | ü
10 | Investigation room | 8 | x | 11 | 88 | Check the vital sciences and non-contact Tonometry | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü
11 | Multipurpose room | 8 | x | 11 | 88 | Vision, refraction, NCT and center field vision examination | ü | ü
12 | Manual biometry /IOL master | 6 | x | 11 | 66 | Kerotometer, A Scan |  |  | ü | [8 empty] | ü
IV | Investigation area
13 | Labortory |  |  |  |  | To collect specimen and perform necessary tests (biochemistry, micro-biology & pathology) |  | ü | ü | ü | ü | ü | ü | ü |  |  |  |  | Type of tests performed depends on patient profile & volumes handled
14 | Duct, scrapping and pachymetry room | 8 | x | 11 | 88 | Pre examination procedure |  |  |  | ü |  | ü
15 | HFA room | 5 | x | 11 | 55 | Humphrey field / nerve fibre analyzer examination |  |  |  | ü | [8 empty] | Same applies for HRT too
17 | Specular microscopy | 6 | x | 11 | 66 | Scan for eye examination | [5 empty] | ü
18 | Zywave, orbscan room | 8 | x | 11 | 88 | Examination for lasik procedure | [5 empty] | ü
19 | Pentacom room | 6 | x | 11 | 66 | Scan for eye examination | [5 empty] | ü
20 | Confocal room | 6 | x | 11 | 66 | Scan for eye examination | [5 empty] | ü
21 | CCT room | 6 | x | 11 | 66 | Central corneal thickness examination room | [5 empty] | ü
22 | OCT room | 5 | x | 11 | 55 | Anterior OCT retina examination |  |  |  | ü |  |  | ü
23 | FFA room | 8 | x | 11 | 88 | Fundus flouresence angiography laser procedure | [6 empty] | ü
24 | USG and UBM | 10 | x | 11 | 110 | Ultrasonography examination | [6 empty] | ü
25 | ERG room | 10 | x | 11 | 110 | Electro retinogram | [6 empty] | ü
26 | ERG recovery room | 10 | x | 11 | 110 | Recovery room for electro-retinogram | [6 empty] | ü
V | Procedure area
27 | Dilatation area |  | x |  | 0 | Waiting area post dilatation | ü | ü | ü | ü |  |  | ü | ü
28 | YAG laser | 8 | x | 11 | 88 | Laser procedure |  |  | ü | ü
29 | Typical laser room for retina | 8 | x | 11 | 88 | Laser procedure | [6 empty] | ü
30 | Ocular prosthetic room |  | x |  | 0 | False eye installation procedure | [7 empty] | ü
31 | Vision stimulation room | 8 | x | 11 | 88 | Examination and evaluation procedure | [8 empty] | ü
VI | Others
32 | Counselling room | 8 | x | 11 | 88 | Post final examination counselling | ü | ü | ü | ü | ü | ü | ü | ü | ü | ü |  | ü
Recommendations
1) | The following diagnostic equipment require specific operating eco-system - lighting, temperature, etc.
a | HFA
b | HRT
c | FFA
d | USG/UBM
e | ERG
2) | Laser equipment (Yag, Green laser, etc.) - Restricted movement
3) | If the outpatient department includes (a) minor OT, (b) administering Intra-vitreal injections, the layout should be designed to practice asepsis protocol
Note on A8: ====== ID#AAAAIRi1_Ak design (2021-04-19 10:25:39) design: